Steam Trap Fault Detection (Temperature + Ultrasound + Cycling)

# 1. Overview

Detection based on:
- Inlet/Outlet Temperature
- Ultrasound
- Cycles per minute

# Mechanical Steam Traps (Float & Thermostatic / Inverted Bucket)

Behavior:

- Continuous or semi-continuous discharge

- Separate condensate and steam mechanically

| Fault | Temperature | Ultrasound | Cycles/min |
| --- | --- | --- | --- |
| Normal | ΔT small/stable | Continuous/modulated | Low-stable |
| Failed OPEN | In ≈ Out (hot) | Continuous high | No cycling |
| Failed CLOSED | In hot / Out cold | Silent | No cycles |
| Degraded | Fluctuating | Irregular | Irregular |
| Excessive cycling | Fluctuating | Frequent pulses | High |

# Thermodynamic Steam Traps (Disc)

Behavior:

- Operate in cycles (open/close)

- Short bursts of discharge

| Fault | Temperature | Ultrasound | Cycles/min |
| --- | --- | --- | --- |
| Normal | Fluctuating | Pulsed regular | Moderate |
| Failed OPEN | In ≈ Out (hot) | Continuous | No cycles |
| Failed CLOSED | In hot / Out cold | Silent | No cycles |
| Short cycling | Rapid fluctuation | Very frequent pulses | High |
| Excessive cycling | Fluctuating | Very fast pulses | Very high |

# Thermostatic Steam Traps (Bellows)

Behavior:

- Open/close based on temperature difference

- Discharge cooler condensate

| Fault | Temperature | Ultrasound | Cycles/min |
| --- | --- | --- | --- |
| Normal | Out < In | Low/intermittent | Low |
| Failed OPEN | Out ≈ In | Continuous | No cycles |
| Failed CLOSED | Out cold | Silent | No cycles |
| Degraded | Unstable ΔT | Irregular | Irregular |
| Excessive cycling | Fluctuating | Frequent pulses | High |